## progressive tripping (hidden)
T007 Parali Thermal Power Station
TRIPPING REPORT FOR THE PERIOD : 01/04/2016 To 31/03/2017
SNO | UNIT | NATURE | TRIPPING Date | TRIPPING Time | SYN. Date | SYN. Time | HOUR | GEN. LOSS | REASON
1 | UNIT06 |  | 22.10.2016 | [5 empty] | M.s.TEMP PROBLEM
2
3
4
5
6
7
8
9
10
11
12
13
14
1 | UNIT07 | FORCED | 22/09/2016 | 13:47 Hrs | 18.10.2016 | 13:29 Hrs |  |  | Set was forced withdrawn due to L D Backing
2 |  | FORCED | 18/10/2016 | 22:22 Hrs | 19.10.2016 | 02:48 Hrs |  |  | Drum Level Very High
3
4
5
6
7
8
9
10
11
12
13
14

## Detail Event Report
Critical Tripping of Unit # 6- NPTPS
U-6
SR. NO | Tripping Date | Tripping Time | SYN. Date | SYN. TIME | Outage Hours | Gen Loss | Reason | Short term plan | Long term plan
11
12
13
14
15
16
17
18
19
20
1 | 26/08/2008 | 23:27 | 31/08/2008 | 13:17 | 733.17 | 183.321 | Unit Withdrawn for Annual Overhaul work & also to check HPT Shaft Vibration. It is decided by M/s. BHEL during overhaul LPT to be opened & inspection to be carried out. |  | AOH Carried out
2 | 31/08/2008 | 13:45 | 2008-02-09 | 13:53 | 48:08 | 12.034 | TA Set handtripped due to HPT-R shaft vibration increased.Matter referred to M/s. BHEL for raising in HPT-R Vibration. | Under Observation of BHEL, HPT-R Vibration checking done | ----
3 | 2008-02-09 | 14:32 | 13/11/2008 | 8:41 | 1722:09 | 430.05 | TA Set handtripped due to HPT-R shaft vibration increased. ( 201 to 222 micron) | As per M/s. BHEL, Opening of IP Turbine for internal inspection. | After opening of IP Turbine, it was found that: 1) a)IP Rotor 8th stage lock blade found missing. b)Blade (particles) materials deposit observed in the casing between guide 8 & 9. c)Broken blade lock screw found stuck up in between the rotor sealing fins. d) Three no blades adjustment to lock blade found to have damaged. e) IP casing guide blades stage no. 8 & 9 of both top & bottom casing were found having severe dent marks. f) few guide blades both top & bottom near to casing parting plane found have axially shifted. g) sealing fins between guide blade stages 8 & 9 found washed off. h) Minor rubbing mark observed in the leading edge near to shroud of 7th stage moving blade. i)All other stage lock blades are found intact. As such it is decided to replaced IP module & HP module. IP module & HP module replaced.