## Sheet1
EVENT ANALYSIS REPORT
UNIT NO. 4 | 250 MW SET |  | MSPGCL, TPS PARAS
1. Event No. 02 | Month | June.12 |  | Date |  | 2012-06-30 | Time | 07:01 Hrs
2. Operating condition at the time of Event | Load | 230 MW | Coal cycles in service |  |  | AB & CD
| Oil support in service |  |  |  |  | Nil
3. Nature of event : | TA set withdrawn due to Heavy oil leakage near MOT through JOP discharge sensing line of pressure transmitter.
4. Last Tripping : | Load | 160 MW | Time | 3:51 | Hrs | Date | 2012-06-26
Details & Remedial actions: | 1. T/A Set tripped on Generator Electrical Protection. During excitation voltage building turbine was tripped on Electrical protection. 2. Faulty B.phase PT-2 replaced and checked by slow voltage build-up and found ok. 3. Boiler lighted up on 26/06/2012 at 06:05 Hrs & set synchronised on 26/06/2012 at 14:45 Hrs.
5. Similar event occurred last time & Remedial actions: | Nil
6. Observation For Present Event: | Heavy oil leakage observed near MOT through JOP discharge sensing pipeline to pressure transmitter. MOT level found dropping from 710mm to 436mm in PCR.
7. Remedial actions / Work carried out | The leakage attended by welding new spool piece on withdrawl of oil system. Turbine bearings No 1,2 & 4 checked for healthiness in consultation with BHEL .
8. Root Cause & Analysis in details: | Material failure of JOP discharge pressure sensing pipeline was observed .
9. Preventive action suggested short term : | The damaged pressure sensing pipeline is replaced by new spool piece by welding.
10.Preventive action suggested long term: | Nil
11. Boiler lighted up : | Date |  | 2012-07-09 |  | Time |  | 04:21 Hrs.
12.TASet synchronised: | Date |  | 2012-07-09 |  | Time |  | 15.05 Hrs.
13. Remark:
Chief Engineer
S.E.(Op.I/II) S.E.(M/CHP) Dy.C.E.
Chief Engineer